## ReadingTable
Index | Signal | Comment | Description | Resolution | Unit of measure | Hexadecimal address | Decimal address | Data type
1 | Turbine state |  | See table 2 | 1 |  | 201 | 513 | INT
2 | Status information |  | See table 3 | 1 |  | 202 | 514 | INT
3 | Electrical power output |  |  | 0.1 | kW | 203 | 515 | INT
4 | Site imported electrical power | Needs external measurement, optional |  | 0.1 | kW | 204 | 516 | INT
5 | Site water temperature |  |  | 0.1 | °C | 205 | 517 | INT
6 | Site boiler outlet temperature | Needs external measurement, optional |  | 0.1 | °C | 206 | 518 | INT
7 | Exhaust gas temperature | Needs external measurement, optional |  | 0.1 | °C | 207 | 519 | INT
8 | Heat exchanger inlet water temp | Needs external measurement, optional |  | 0.1 | °C | 208 | 520 | INT
9 | Heat exchanger outlet water temp |  |  | 0.1 | °C | 209 | 521 | INT
10 | Heat exchanger bypass position |  | Opening of by-pass on the exhaust gas | 0.1 | % open | 020A | 522 | INT
11 | Turbine speed |  | Percentage of speed (0–100%) ≈ (0–70,000 rpm) | 0.1 | % | 020B | 523 | INT
12 | Mechanical vibration |  |  | 0.01 | g | 020C | 524 | INT
13 | Fuel valve inlet pressure |  |  | 0.01 | bar | 020D | 525 | INT
14 | Air filter pressure drop |  |  | 1 | Pa | 020E | 526 | INT
15 | Pilot valve cmd |  |  | 0.1 | % | 020F | 527 | INT
16 | Main valve cmd |  |  | 0.1 | % | 210 | 528 | INT
17 | Air inlet temperature |  |  | 0.1 | °C | 211 | 529 | INT
18 | Turbine outlet temperature (TOT) |  |  | 0.1 | °C | 212 | 530 | INT
19 | Generator temperature |  |  | 0.1 | °C | 213 | 531 | INT
20 | PE DC link voltage |  |  | 0.1 | VDC | 214 | 532 | INT
21 | Bearing inlet oil temperature |  |  | 0.1 | °C | 215 | 533 | INT
22 | Ball bearing oil temperature |  |  | 0.1 | °C | 216 | 534 | INT
23 | Roller bearing oil temperature |  |  | 0.1 | °C | 217 | 535 | INT
24 | Operation hours |  |  | 10 | h | 218 | 536 | INT
25 | Running hours |  |  | 1 | h | 219 | 537 | INT
26 | Number of starts |  |  | 1 |  | 021A | 538 | INT
27 | Produced electrical energy |  |  | 1000 | kWh | 021B | 539 | INT
28 | Produced electrical energy (ext) | Needs external measurement, optional |  | 1000 | kWh | 021C | 540 | INT
29 | Consumed gas volume (ext) | Needs external measurement, optional |  | 1000 | m³/h | 021D | 541 | INT
30 | Produced thermal energy (ext) | Needs external measurement, optional |  | 1000 | kWh | 021E | 542 | INT
31 | PMC – digital input bit word | bit word | See table 4 | 1 |  | 021F | 543 | UINT
32 | SCC – digital input bit word | bit word | See table 4 | 1 |  | 220 | 544 | UINT
33 | Fault word 1 | bit word | See table 5 | 1 |  | 221 | 545 | UINT
34 | Fault word 2 | bit word | See table 5 | 1 |  | 222 | 546 | UINT
35 | Fault word 3 | bit word | See table 5 | 1 |  | 223 | 547 | UINT
36 | Fault word 4 | bit word | See table 5 | 1 |  | 224 | 548 | UINT
37 | Fault word 5 | bit word | See table 5 | 1 |  | 225 | 549 | UINT
38 | Fault word 6 | bit word | See table 5 | 1 |  | 226 | 550 | UINT
39 | Fault word 7 |  | Not used |  |  | 227 | 551 | UINT
40 | Active control mode | Local / BMS / Remote / Schedule / SiteCtrl / Modbus |  | 1 |  | 228 | 552 | INT
41 | Running hours (fine reading) |  | Value to add to reg. 25 to have complete read | 0.001 | h | 229 | 553 | –
42 | Not used |  |  |  |  | 022A | 554 | –
43 | Not used |  |  |  |  | 022B | 555 | –
44 | Not used |  |  |  |  | 022C | 556 | –
45 | Not used |  |  |  |  | 022D | 557 | –
46 | Buffer air pressure |  |  | 1 | mbar | 022E | 558 | INT
47 | EEI Aux Inv 3° Phase |  |  | 0.1 | A | 022F | 559 | INT
48 | CNG Fuel Booster speed |  |  | 0.1 | RPM | 230 | 560 | INT
49 | Not used |  |  |  |  | 231 | 561 | –
50 | Not used |  |  |  |  | 232 | 562 | –

## InternalState
State number | Denomination | Description
1 | STOPPED | The unit is stopped. Main contactor is opened.
2 | CHECK GAS | Check of gas leakage.
3 | VENTILATION WITHOUT ENCLOSURE LOAD | The ventilation fan is running and the enclosure loads are not supplied.
4 | VENTILATION WITH ENCLOSURE LOAD | Enclosure evacuation fan is in operation. Also active when unit is cooling down after running.
5 | START AUX SYSTEMS | Enclosure electrical systems are powered up.
6 | RAMP UP | Speed is increased from 0% to 35%.
7 | VENTILATION | Turbine system is ventilated from gas.
8 | LIGHT UP | Gas flow is enabled and combustion chamber is ignited.
9 | RAMP UP 2 | Speed is increased from 35% to 75%.
10 | POST START RAMP | Recuperator and heat exchanger warmed up with a slow increasing temperature ramp.
11 | RUNNING | Unit is in full operation and reacts to user-defined power and water temperature requests.
12 | STOPPING | The speed is decreased till 0%.
13 | VENTILATION WITH ENCLOSURE LOAD | The ventilation fan is running and the enclosure loads are supplied.
14 | VENTILATION WITHOUT ENCLOSURE LOAD | The ventilation fan is running and the enclosure loads are not supplied.
15 | STOPPED WITH ALARM | Turbine is stopped and an alarm is active.

## Status
Status information | Description
0 | No information
1 | Emergency active
2 | Test mode active
3 | Alarm active
4 | Stopped for service
5 | Main switch open
6 | Stopped by BMS
7 | PE power limitation
8 | Diff. Press. not set
9 | Date not set
10 | Grid not healthy (ext.)
11 | Grid mode not enabled
12 | BMS Grid mode not enabled
13 | Electrical power demand low
14 | Heat demand low
15 | Braked mod. not available
16 | Main contactor open
17 | BMS level stop
18 | Grid healthy (int)
19 | SAM not enabled
20 | BMS — SMA not enabled
21 | PE not of SAM type
22 | SA grid not healthy
23 | Start battery low volt
24 | not used
25 | not used
26 | RunlnMode operation
27 | Shut down in progress
28 | Grid mode operation
29 | Stand Alone mode operation
30 | HSB operation
31 | Gen mode not selected